## user_inputs
Parameter | Value | Unit | Scope | Meaning
N | 3 | y | Normal | Number of time series to generate for contingencies
MTTR_genac | 50 | h | Normal | MTTR for Generator
FOR_genac | 0.03 | % | Normal | Unavailability rate for Generator
MTTR_trac | 768 | h | Normal | MTTR for Transformer
FOR_trac | 0.02 | % | Normal | Unavailability rate for Transformer
MTTR_convdc | 50 | h | Normal | MTTR for Converter
FOR_convdc | 0.05 | % | Normal | Unavailability rate for Converter
MTTR_ohlac | 16 | h | Normal | MTTR for AC OHL
MTTR_ohlac_resil | 2880 | h | Extreme | MTTR for AC OHL (extreme events)
failurerate_fixe_ohlac | 0.22 | 1/y | Normal | Annual failure rate for AC OHL (fix share)
failurerate_perkm_ohlac | 0.00832 | 1/y/km | Normal | Annual failure rate for AC OHL (per km share)
MTTRbr_ohldc | 30 | h | Normal | MTTR for DC OHL
MTTRbr_ohldc_resil | 2880 | h | Extreme | MTTR for DC OHL (extreme events)
failurerate_fixe_ohldc | 0.1 | 1/y | Normal | Annual failure rate for DC OHL (fix share)
failurerate_perkm_ohldc | 0.0005 | 1/y/km | Normal | Annual failure rate for DC OHL (per km share)
MTTR_cabledc | 1500 | h | Normal | MTTR for DC cable
MTTR_cabledc_resil | 1500 | h | Extreme | MTTR for DC cable (extreme events)
failurerate_perkm_cabledc | 0.0007 | 1/y/km | Normal | Annual failure rate for DC cable (per km share)