## user_inputs
Attribute | MTTR | FOR | Failure rate 0 | Failure rate per km | Correlation between poles
Unit | h | % | 1/y | 1/y/km | Number between 0 & 1
Description | Mean Time To Repair for normal event | Forced Outage Rate (unavailability rate). 0.01 means 1% of the time. | Failure rate for 0 km | Additional failure rate per km | 0: no correlation. 1: perfect correlation /!\ Correlation >0 is allowed only if you use Matlab (not Octave) and have the toolbox "Statistics and Machine Learning Toolbox"
Generator | 50 | 0.03
Transformer | 768 | 0.02
Converter ACDC | 50 | 0.05 |  |  | 0
AC OHL | 16 |  | 0.22 | 0.00832
DC OHL | 30 |  | 0.1 | 0.0005 | 0
DC cable | 1500 |  | 0 | 0.0007 | 0